## Slide 1
Stealthy Attack & Resilient
Defense on the SWaT Testbed
51.508 Secure Cyber Physical Systems | Project Proposal
Modbus False Command Injection
Constrained Concealment Evasion
Invariant-Based Recovery
iTrust Lab | SWaT Testbed | AY2025/26 Term 2

## Slide 2
Project Overview
01
Motivation
SWaT uses Modbus/EtherNet-IP with no auth. Existing ML detectors are vulnerable to adversarial evasion.
02
Attack
Stealthy Modbus false command injection targeting pumps & valves with sensor spoofing to evade anomaly detection.
03
Defense
Hybrid detector: process invariants (physics-based) combined with a reconstruction-based ML autoencoder.
04
Recovery
Automated safe-state transition + hot-standby PLC failover + invariant-guided sensor reconstruction.
Research Contribution: First end-to-end demonstration on SWaT combining adversarial evasion attacks with a hybrid physics+ML defense and automated recovery.

## Slide 3
Threat Model & Assumptions
Attacker Profile
Access:
Network-level access to Level 1/2 OT network (e.g. via compromised engineering workstation or rogue laptop on switch)
Knowledge:
Knows Modbus register map (obtainable via passive sniffing). Black-box knowledge of anomaly detector.
Capability:
Can intercept, inject, and spoof Modbus TCP frames. Can manipulate sensor readings reported to SCADA HMI.
Goal:
Cause physical damage (tank overflow / pump cavitation) without triggering alarms for as long as possible.
SWaT Attack Surface
Zone D (IT)
SCADA workstation — initial foothold via phishing or rogue device
Firewall
Traversal possible if SCADA talks to OT — common misconfiguration
Zone B (OT)
Modbus/TCP to PLC1–PLC6, no authentication — direct command injection
Zone A (SIS)
Safety Instrumented System — target is to stay below SIS thresholds

## Slide 4
Attack Design
Papers #9 (Modbus FCI) + #31 (Constrained Concealment)
Phase 0
Reconnaissance
Passive Wireshark sniff on
Modbus TCP port 502.
Map PLC IPs, register
addresses, I/O tags.
▶
Phase 1
False Command
Inject crafted Modbus
write-coil/register frames
e.g. close MV101, force
P101 pump OFF.
▶
Phase 2
Sensor Spoofing
Replay captured legitimate
responses to SCADA HMI (Paper #9 Algorithm 1).
Additionally spoof sensor values
via adversarial AE to evade ML detectors (Paper #31).
Target: SWaT P1 (raw water intake) → force MV101 closed + P101 OFF while LIT101 shows normal level → starvation of downstream stages P2–P6

## Slide 5
Why Existing Detectors Fail
ML-Only Anomaly Detector
(e.g. reconstruction autoencoder)
✗ Learns normal sensor correlations from training data
✗ Paper #31 adversarial autoencoder crafts sensor perturbations that minimise MSE reconstruction error
✗ Black-box attack — no need to know model internals
✗ Operates in milliseconds — meets real-time Modbus constraints
✗ Detection rate drops to near-zero under constrained concealment
Invariant-Only Detector
(e.g. SWaT DAD / Adepu & Mathur)
✗ Encodes physics-based rules from P&ID (e.g. if P101 ON → FIT101 > threshold)
✗ Catches gross physical violations but misses low-rate stealthy changes
✗ AICrit only detected 24/36 attacks in SWaT dataset (Adepu et al.)
✗ Attacker can stay within invariant bounds by manipulating slowly
✗ No ML component means blind to novel multi-sensor coordinated spoofing

## Slide 6
Defense Design
Hybrid Invariant + ML Anomaly Detection
Sensor &
Actuator Readings
▶
Process Invariant
Checker (Physics)
▼
Reconstruction
Autoencoder (ML)
▶
Decision Fusion
(AND / weighted vote)
▶
ALERT
→ Trigger Recovery
Example Invariants for P1:
IF MV101=OPEN AND P101=ON THEN FIT101 > 0.4 m³/h within 10s
IF LIT101 < LOW_THRESHOLD THEN P101=OFF (tank protection invariant)
IF P101=OFF AND MV101=CLOSED THEN LIT101_rate_of_change ≈ 0 (no spurious flow)

## Slide 7
Recovery Design
1
Detect
Hybrid detector raises alert. Affected P-stage and compromised sensors identified.
▶
2
Contain
Block malicious Modbus frames at network layer. Isolate compromised PLC channel.
▶
3
Safe State
Transition affected stage to pre-defined safe config. Fail-safe valve/pump positions per P&ID.
▶
4
Failover
Hot-standby PLC takes over. Switches to local sensor reads, bypasses compromised network path.
▶
5
Verify & Resume
Cross-validate sensors via invariant model. Gradually restore normal operation stage-by-stage.
SWaT Safe State Configuration (per stage):
Stage | Safe Valve State | Safe Pump State
P1 – Raw Water | MV101: CLOSED | P101: OFF
P2 – Pre-Treatment | P201–P206: ALL OFF | P102: OFF (P1 backup pump)
P3 – Ultrafiltration | MV301: CLOSED | P301/302: OFF
P4 – De-chlorination / P6 – RO | UV401: OFF / P602: OFF | Hold / RO pump OFF

## Slide 8
Implementation Plan
Week 9–10
Phase 1: Setup & Attack
-> Deploy Wireshark on SWaT Level 1/2 switch mirror port
-> Map Modbus register addresses for P1 actuators (MV101, P101)
-> Implement Python-based Modbus injection script (port 502)
-> Verify false commands reach PLC — confirm physical effect on SWaT
-> Capture baseline sensor timeseries for autoencoder training
Week 11
Phase 2: Evasion & Defense
-> Train reconstruction autoencoder on SWaT normal operation data
-> Implement adversarial perturbation (Paper #31 learning-based method)
-> Verify attack evades standalone ML detector
-> Derive process invariants for P1–P3 from SWaT P&ID
-> Implement invariant checker + combine with autoencoder (decision fusion)
Week 12–13
Phase 3: Recovery & Demo
-> Implement safe-state transition logic for P1 (trigger on alert)
-> Configure hot-standby PLC failover (using SWaT dual-PLC architecture)
-> Implement sensor cross-validation using invariant reconstruction model
-> Run full end-to-end demo: attack → evade → detect → recover
-> Measure recovery time (KPI: time from alert to normal operation)
Tools: Python (Scapy/pyModbus) · Wireshark · PyTorch (autoencoder) · Studio 5000 (PLC) · SWaT SCADA HMI

## Slide 9
Evaluation Metrics
Attack Effectiveness
▸ Time-to-impact: how quickly does tank level deviate from normal?
▸ Evasion rate: % of attack cycles that pass through standalone ML detector undetected
▸ Stealth duration: time elapsed before any alert is raised
Detection Performance
▸ Detection rate (DR): % of attack scenarios detected by hybrid detector
▸ False positive rate (FPR): % of normal operation flagged as anomalous
▸ Comparison: invariant-only vs ML-only vs hybrid (DR & FPR)
Recovery Performance
▸ Recovery time (RT): seconds from alert to restored normal operation
▸ Sensor trust accuracy: % of spoofed sensors correctly identified via invariant cross-validation
▸ Physical integrity: no unsafe state (overflow/underflow) during recovery window
Bonus Evaluation: Apply our defense against another group's attack (cross-group exercise as per course rubric)

## Slide 10
References
[1]
W. Alsabbagh, S. Amogbonjaye, D. Urrego, and P. Langendörfer
"A Stealthy False Command Injection Attack on Modbus based SCADA Systems"
IEEE CCNC, Las Vegas, USA, Jan. 2023.
[2]
J. H. Castellanos, M. Ochoa, A. A. Cardenas, O. Arden, and J. Zhou
"Constrained Concealment Attacks against Reconstruction-based Anomaly Detectors in ICS"
ACM ACSAC, Austin, USA, Dec. 2020. | github.com/scy-phy/ICS-Evasion-Attacks
[3]
S. Adepu and A. Mathur
"Using Process Invariants to Detect Cyber Attacks on a Water Treatment System"
IFIP SEC, Ghent, Belgium, May 2016.
[4]
S. Adepu and A. Mathur
"Distributed Detection of Single-Stage Multipoint Cyber Attacks in a Water Treatment Plant"
ACM AsiaCCS, Xi'an, China, May 2016.
[5]
C. M. Ahmed, J. Zhou, and A. P. Mathur
"Attacking Fieldbus Communications in ICS: Applications to the SWaT Testbed"
Singapore Cyber Security R&D Conference (SG-CRC), Singapore, 2016.
[6]
A. Carcano, A. Coletta, M. Guglielmi, M. Masera, I. N. Fovino, and A. Trombetta
"A Multidimensional Critical State Analysis for Detecting Intrusions in SCADA Systems"
IEEE Trans. Industrial Informatics, vol. 7, no. 2, pp. 179–186, May 2011. DOI: 10.1109/TII.2010.2098415
[7]
D. I. Buzhinsky and V. Vyatkin
"Automatic Inference of Finite-State Plant Models from Traces and Temporal Properties"
IEEE Trans. Industrial Informatics, vol. 13, no. 4, pp. 1521–1530, Aug. 2017. DOI: 10.1109/TII.2017.2670001
[8]
A. Humayed, J. Lin, F. Li, and B. Luo
"Cyber-Physical Systems Security: A Survey"
IEEE Internet of Things Journal, vol. 4, no. 6, pp. 1802–1831, Dec. 2017. DOI: 10.1109/JIOT.2017.2703172
[9]
iTrust, Centre for Research in Cyber Security, SUTD
"SWaT: Secure Water Treatment Testbed"
Singapore University of Technology and Design. https://itrust.sutd.edu.sg/testbeds/secure-water-treatment-swat/
51.508 Secure Cyber Physical Systems | References

## Slide 11
SWaT P1 Attack
False Command Injection via Modbus MITM
Based on Alsabbagh et al., IEEE CCNC 2023 (Paper #9)
Phase 0: Recon
Phase 1: Inject
Phase 2: Conceal
Target: PLC1 (P1 stage) — Force MV101 CLOSED + P101 OFF via unauthenticated Modbus writes
Scripts
phase0_recon.py
phase1_inject.py
phase2_spoof.py
Python / Scapy
pyModbus / PyTorch
51.508 Secure CPS · SWaT Attack Implementation · Overview

## Slide 12
SWaT P1 — What We Are Attacking
Raw Water Intake Stage · PLC1 · Modbus TCP port 502
51.508 Secure CPS · SWaT Attack Implementation · Slide 12/18 — Architecture

## Slide 13
Threat Model & Attack Surface
Attacker Profile
Access level
Zone D (IT network) — realistic via USB/phishing (TRITON, BlackEnergy precedent)
Goal
Disrupt P1 water intake; starve downstream P2–P6 stages
Tools
Scapy, pyModbus, arpspoof — all standard Python
Knowledge
Modbus spec is public; no PLC vendor credentials needed
Stealth
HMI operator sees nothing — fake responses replayed from pre-built DB
Why Modbus Has No Defence
No Auth
Any device on the network can write coils/registers to any PLC
Plaintext
Frames transferred in clear — Wireshark reveals everything
No timestamp
Devices cannot tell if a response is current or a replay
No integrity
Frame contents can be altered; PLC cannot detect manipulation
Open spec
Modbus protocol reference is freely downloadable — attacker has full spec
51.508 Secure CPS · SWaT Attack Implementation · Slide 13/18 — Threat Model

## Slide 14
Phase 0
Reconnaissance & Database Building
phase0_recon.py · NMAP SYN scan + Wireshark-style Modbus capture (~30 min)
Step 1 — NMAP SYN Scan
nmap -sS -p 502 192.168.1.0/24
SYN (half-open) scan — does not complete TCP handshake.
Harder to detect by default firewall rules.
Finds all PLCs with port 502 open.
Step 2 — Capture & Pair Modbus Frames
Match by: TID + Unit ID + Func Code
Sniff for ~30 min. Each HMI→PLC request is paired with its PLC→HMI response using 3 shared fields (Paper #9 Fig.5). Duplicates removed. Result: dict of request-response pairs.
Modbus TCP Frame (Paper #9 Fig. 2)
Trans ID
2B
Proto ID
2B
Length
2B
Unit ID
1B
Func Code
1B
Data
≤248B
← Matching key for DB pairing →
51.508 Secure CPS · SWaT Attack Implementation · Slide 14/18 — Phase 0: Recon

## Slide 15
Phase 1
ARP Poisoning + False Command Injection
phase1_inject.py · Scapy ARP spoof + pyModbus write to PLC1:502
ARP Poisoning — MITM Setup
Tell HMI: "PLC1's IP → my MAC"
Tell PLC:
"HMI's IP → my MAC"
All traffic now routes through attacker.
Re-broadcast every 1.5s to maintain MITM.
IP forwarding enabled on attacker machine.
False Command Injection
client.write_coil(MV101_CLOSE, True)
client.write_coil(P101_STOP, True)
Python pyModbus sends crafted Modbus frames to PLC1:502. No authentication required — PLC accepts any write from any device on the network.
Algorithm 1 — Concealment (Paper #9) · Replay DB responses to HMI while injecting PLC
for each packet sniffed from network:
if src==HMI and dst==PLC and port==502:
drop original request # do not forward to PLC
response = db.lookup(unit_id, func_code) # O(1) hash lookup
send forged_response → HMI # operator sees nothing
send false_command → PLC # PLC obeys attacker
51.508 Secure CPS · SWaT Attack Implementation · Slide 15/18 — Phase 1: Inject

## Slide 16
Phase 2
Adversarial Sensor Spoofing — Evading ML Detectors
phase2_spoof.py · Castellanos et al., ACSAC 2020 (Paper #31) · github.com/scy-phy/ICS-Evasion-Attacks
Problem: Naive Replay
✗ Phase 1 replays static stored values
✗ Physical correlations break: LIT101 stays flat while P101 is OFF
✗ Reconstruction AE detects increasing MSE error over time
✗ Paper #31: triggers alarms when <95% sensors are manipulated
Solution: Adv. Autoencoder
Learning-based (black-box):
Train adversarial net to output perturbation δ such that:
AE_detector(x + δ)
has low reconstruction error
→ looks normal to detector
Constraint: ||δ||∞ ≤ ε
Runs in milliseconds
— meets Modbus timing window
Training Loss
L = α · MSE_detector(x+δ)
+ β · ||δ||₂
α·MSE → fool detector β·||δ|| → keep perturbation small Result: spoofed sensor values that reconstruct normally through any AE detector
51.508 Secure CPS · SWaT Attack Implementation · Slide 16/18 — Phase 2: Evade

## Slide 17
Implementation Scripts — Usage Reference
phase0_recon.py
NMAP SYN scan + Modbus packet sniffer + request-response DB builder
sudo python3 phase0_recon.py \
--subnet 192.168.1.0/24 \
--iface eth0 --duration 1800 \
--db modbus_db.pkl
deps: scapy python-nmap
out: modbus_db.pkl swat_capture.pcap recon_results.json
phase1_inject.py
ARP poisoning MITM + false Modbus coil writes + Algorithm 1 concealment replay
sudo python3 phase1_inject.py \
--plc-ip 192.168.1.10 \
--hmi-ip 192.168.1.20 \
--db modbus_db.pkl --duration 120
deps: scapy pymodbus
out: Console: injection count + concealment events
phase2_spoof.py
Adversarial autoencoder: train detector + adv model, then spoof sensor readings at attack time
python3 phase2_spoof.py train \
--data swat_normal.csv --epochs 100
python3 phase2_spoof.py attack \
--plc-ip 192.168.1.10 --adv-model adv_model.pt
deps: torch numpy pandas scapy pymodbus scikit-learn
out: detector.pt adv_model.pt
51.508 Secure CPS · SWaT Attack Implementation · Slide 17/18 — Scripts

## Slide 18
Before You Run — Practical Notes for SWaT
Pre-Run Checklist
Confirm Modbus TCP is enabled on SWaT PLC1 (ask lab engineer)
Get register addresses for MV101 + P101 from Phase 0 sniff — do NOT guess
Get iTrust lab engineer sign-off before running ARP poisoning
TA must be physically present during all experiments
Run Phase 0 first — never inject without the pre-built DB
Test injection on digital twin before live SWaT
Document clean-exit: restore_plc_state() runs automatically on stop
P1 Register Map (fill from Phase 0)
MV101_CLOSE
0x????
Coil — close motorised valve
P101_STOP
0x????
Coil — stop pump P101
LIT101
0x????
Holding reg — tank level
FIT101
0x????
Holding reg — flow sensor
Race Condition (Paper #9 §IV-B)
Your forged HMI response must arrive before the real PLC response. Pre-key the database as dict keyed on (unit_id, func_code) for O(1) lookup. SWaT polling cycle ≈ 1–2s — you have margin.
Dual PLC Note
SWaT has primary + hot-standby PLCs per stage. Target primary; standby takeover is your recovery trigger.
51.508 Secure CPS · SWaT Attack Implementation · Slide 18/18 — Notes

## Slide 19
Defending SWaT
Against Stealthy Modbus False Command Injection
Layer 1
Process Invariant Checker
Layer 2
Reconstruction Autoencoder
Layer 3
Decision Fusion + Alert
Recovery: Detect → Contain → Safe State → PLC Failover → Invariant-Verified Resume
51.508 Secure Cyber Physical Systems | iTrust Lab, SUTD | AY2025/26 Term 2
51.508 Secure CPS · SWaT Defense Architecture

## Slide 20
Why Single-Layer Defenses Fail
Each defense alone is evaded by our attack — which is exactly why the hybrid exists
ML-Only Anomaly Detector
e.g. Reconstruction Autoencoder (BATADAL baseline)
✗
Learns normal correlations from training data only
✗
Paper #31 adversarial AE crafts δ minimising MSE recon error
✗
With |δ|∞ ≤ ε = 0.1, evasion rate ~94% on SWaT
✗
Sensor spoof looks normal to the ML model's latent space
✗
Blind to actuator state — only sees sensor timeseries
Invariant-Only Detector
e.g. Adepu & Mathur, IFIP SEC 2016 (Papers #88)
✗
Physics rules encode P&ID constraints (e.g. MV101 open → FIT101 > 0)
✗
Paper #9 Phase 2 replay sends stale-but-valid sensor readings
✗
Only 24 of 36 SWaT attacks detected by invariant alone [Adepu 2016]
✗
No timing anomaly flagged if replay matches polling frequency
✗
Cannot detect gradual drift if attacker moves slowly within bounds
Conclusion: Neither layer alone is sufficient. The hybrid forces the attacker to simultaneously satisfy physics constraints AND fool the ML detector — a much harder constraint.

## Slide 21
Hybrid Defense Architecture
Three cooperative layers — each compensates for the other's blind spots
SWaT
Sensor &
Actuator
Readings
→
Layer 1
Process Invariant
Checker
Physics-based rules
from SWaT P&ID
(Adepu & Mathur 2016)
→
Layer 2
Reconstruction
Autoencoder
ML anomaly score
vs learned normal
distribution
→
Layer 3
Decision
Fusion
Weighted vote +
alert + trigger
recovery pipeline
↓ ALERT + RECOVERY TRIGGER
Layer 1 — What it checks
▸ MV101 OPEN → FIT101 > 0.5 m³/h
▸ P101 ON → LIT101 rising or stable
▸ LIT101 < HIGH_LIMIT → P101 ON
▸ P101 OFF → LIT101 falling (drain only)
▸ MV101 CLOSED + P101 ON = invariant violation
Layer 2 — Autoencoder
▸ Trained on 7 days normal SWaT data
▸ Encoder: 50→32→16→8 (latent dim)
▸ Anomaly score = MSE(x, x̂)
▸ Threshold = 95th pctile of train errors
▸ Raises flag if score > threshold
Layer 3 — Fusion logic
▸ ALERT if inv_flag fires (score ≥1.5) or both fire together
▸ WARN if AE alone fires (score=1.0 < threshold) — investigate
▸ Invariant flag weighted ×1.5 (physics > stats)
▸ 3-cycle confirmation window (anti-flap)
▸ Trigger recovery if ALERT confirmed
51.508 Secure CPS · SWaT Defense · Architecture

## Slide 22
Layer 1 — Process Invariant Checker
Physics-based rules derived from the SWaT P&ID — cannot be fooled by ML evasion
#
Condition
Invariant Rule
Physical Reason
I-1
MV101 OPEN
FIT101 > 0.4 m³/h
Water flows when valve open
I-2
P101 ON
FIT101 > 0.3 m³/h
Pump drives positive flow
I-3
P101 ON
LIT101 not falling rapidly
Pump fills or holds tank
I-4
LIT101 > HIGH (800mm)
P101 OFF within 2 cycles
Overflow protection
I-5
LIT101 < LOW (250mm)
MV101 OPEN + P101 ON
Dry-run protection
I-6
MV101 CLOSED
FIT101 < 0.05 m³/h
No flow when valve shut
I-7
P101 ON + MV101 CLOSED
→ VIOLATION (attack signature)
Impossible physics state
I-8
P101 OFF
LIT101 non-increasing
Tank drains only if pump off
Key insight: I-7 fires immediately when Paper #9 forces P101 ON + MV101 CLOSED simultaneously — the invariant flags the attack before any physical damage occurs.
51.508 Secure CPS · SWaT Defense · Layer 1 — Invariants

## Slide 23
Layer 2 — Reconstruction Autoencoder
Trained on normal SWaT sensor timeseries — flags deviations from learned correlations
Autoencoder Architecture
Input
51 features
(all SWaT sensors, window=10)
↓
Encoder L1
128 units ReLU
↓
Encoder L2
64 units ReLU
↓
Latent z
16 units (bottleneck)
Decoder L1
64 units ReLU
↓
Decoder L2
128 units ReLU
↓
Output x̂
51 features reconstruction
MSE(x, x̂) = Anomaly Score
Training
▸ 7-day SWaT normal operation dataset (iTrust)
▸ Sliding window: 10 timesteps, step=1
▸ Batch size 128, Adam optimiser, lr=1×10⁻³
▸ 100 epochs, MSE loss on reconstruction
▸ Threshold = 95th percentile of training MSE
Detection Logic
▸ At inference: compute MSE(x_t, x̂_t) per timestep
▸ Flag if score > threshold for 3 consecutive steps
▸ Rate of score increase also tracked (gradient check)
▸ Separates genuine anomaly from sensor noise
Why AE Alone Fails (Paper #31)
▸ Adversarial AE trained to minimise our detector's MSE
▸ Perturbation δ constrained to ‖δ‖∞ ≤ 0.1 (imperceptible)
▸ Bypasses AE alone in ~94% of cycles (Paper #31 result)
▸ → Layer 1 invariant catches what AE misses
51.508 Secure CPS · SWaT Defense · Layer 2 — Autoencoder

## Slide 24
Layer 3 — Decision Fusion & Alert
Combines both detection signals — minimises false positives while maximising detection coverage
Invariant Flag
AE Flag
Output
Confidence
Action
Invariant Flag
AE Flag
Output
Confidence
Action
✓ TRIGGERED
✓ TRIGGERED
🔴 ALERT
HIGH (99%)
Initiate full recovery pipeline
✓ TRIGGERED
✗ Clean
🟠 ALERT
HIGH (95%)
Alert + log + verify invariant
✗ Clean
✓ TRIGGERED
🟡 WARN
MEDIUM (70%)
Investigate — possible drift
✗ Clean
✗ Clean
🟢 NORMAL
N/A
Continue normal operation
Weighted Fusion Formula
score_fusion = 1.5 × inv_flag + 1.0 × ae_flag
ALERT if score_fusion ≥ 1.5 (3-cycle window)
Invariant weighted ×1.5 because physics violations are deterministic, not probabilistic.
Timing Constraints (SWaT)
▸ PLC polling cycle: 1–2 seconds
▸ Invariant check: <1 ms (rule lookup)
▸ AE inference: ~8 ms (GPU) / ~45 ms (CPU)
▸ Total detection latency: <50 ms per cycle
▸ 3-cycle confirmation: 3–6 seconds to alert
51.508 Secure CPS · SWaT Defense · Layer 3 — Fusion

## Slide 25
Why the Hybrid Defeats Paper #31's Evasion
The adversarial autoencoder can fool the ML layer — but it cannot satisfy physics simultaneously
The Attacker's Dilemma
Paper #31 trains a perturbation network δ(x) such that:
MSE_detector( x + δ ) ≈ 0
‖δ‖∞ ≤ ε = 0.1
This successfully evades the AE (Layer 2). But:
✗
δ on sensor readings ≠
δ on physical state
The real P101 is still OFF. The real MV101 is still CLOSED. Perturbing sensor readings reported to HMI does not change what the PLC actually commands.
✗
Invariant I-7 checks
actuator register state
Layer 1 reads directly from PLC coil registers — not from Modbus responses replayed to HMI. The attack cannot spoof both simultaneously.
✗
Constraint violation is
deterministic, not probabilistic
P101 ON + MV101 CLOSED is physically impossible regardless of what the sensor timeseries says. Physics does not average over distributions.
Attack Timeline Under Hybrid Defense
t=0s
Phase 0
ARP poisoning begins, MITM established
t=5s
Phase 1
False write: P101 OFF, MV101 CLOSED injected to PLC1
t=6s
L1 FIRES
Invariant I-7 triggers: P101=ON coil state + MV101=CLOSED
t=7s
Phase 2
Adversarial sensor spoof begins — δ injected into Modbus replies
t=8s
L2 evaded
AE reconstruction error stays below threshold (Paper #31 works)
t=10s
ALERT
Fusion: L1 weight=1.5 → threshold crossed → ALERT triggered
t=11s
Recovery
Modbus blocked, safe state set, standby PLC activated
51.508 Secure CPS · SWaT Defense · Defeating Paper #31

## Slide 26
Recovery Pipeline
Five deterministic steps — from detection to verified normal operation
1
Detect
→
▸ Fusion score ≥ 1.5 for 3 consecutive cycles
▸ Timestamp, sensor snapshot, and alert logged
▸ Operator notified via SCADA HMI alarm
2
Contain
→
▸ Drop all Modbus TCP frames on port 502 (iptables rule)
▸ Isolate attacker MAC from Level 1/2 switch (VLAN)
▸ Freeze current PLC output register state
3
Safe State
→
▸ Write safe-state actuator values to PLC1 (see Slide 9)
▸ MV101 → CLOSED, P101 → OFF (P1 safe idle)
▸ Wait 2 polling cycles to confirm registers held
4
PLC Failover
→
▸ Signal hot-standby PLC1B to take control
▸ EtherNet/IP handshake confirms PLC1B is primary
▸ HMI re-mapped to PLC1B IP (automatic switchover)
5
Verify & Resume
▸ Run all 8 P1 invariants against PLC1B readings
▸ Check LIT101 within [250, 800] mm safe range
▸ Resume only if all invariants pass for 5+ cycles
Total recovery time target: < 15 seconds from alert to verified safe state | PLC1B failover < 3 seconds | No unsafe state (overflow/underflow) during window

## Slide 27
Safe State Table & PLC Failover
Exact actuator targets per stage — written to PLC registers before failover handshake
Stage
Actuator
Safe State Value
Physical Reason
SWaT Risk if Wrong
P1
MV101
CLOSED
Stop raw water intake
Tank overflows if left open
P1
P101
OFF
No pump without intake
Dry-run damage to pump
P1
P102
OFF
Backup pump also idle
Redundant — must match P101
P2
P201–206
ALL OFF
No dosing without P1 feed
Chemical overdose to tank
P3
MV301
CLOSED
Isolate UF feed
Overflow in UF vessel
P3
P301/302
OFF
UF pumps off
Membrane pressure spike
P4
UV401
OFF
UV off — no water to treat
UV element overheating
P6
P602
OFF
RO pump off
Reverse osmosis membrane damage
Hot-Standby PLC Failover: SWaT runs dual PLCs per stage (primary + standby). After safe state is written, the standby PLC (PLC1B) takes control via EtherNet/IP primary/secondary handshake. PLC1B has an identical copy of the ladder logic and resumes from the last known safe register state. The compromised PLC1A is isolated from the network until it is re-imaged and verified.
51.508 Secure CPS · SWaT Defense · Safe State & Failover

## Slide 28
Defense Implementation & Evaluation
Concrete code artifacts and metrics for the course project demo at iTrust Lab
Implementation Artifacts
invariant_checker.py
8 P1 invariants, reads PLC1 coil registers via pyModbus
autoencoder.py
Reconstruction AE, train on SWaT CSV, inference + threshold
fusion.py
Weighted voting, 3-cycle window, alert + log output
recovery_agent.py
iptables block, safe-state write, PLC1B failover trigger
autoencoder_detector.py
Live MSE anomaly scoring; outputs /tmp/ae_flag for fusion engine
Evaluation Metrics
Detection Rate (DR)
% attack scenarios caught by hybrid detector
False Positive Rate (FPR)
% normal operation incorrectly flagged
Evasion Rate (ER)
% attack cycles that pass both layers simultaneously
Time-to-Detect (TTD)
Seconds from injection to confirmed ALERT
Recovery Time (RT)
Seconds from ALERT to invariant-verified safe state
Layer Attribution
Which layer fired first — L1 vs L2 vs both
Baseline Comparison
Invariant alone
DR ~67% FPR <1% Evasion ~33%
AE alone
DR ~72% FPR ~5% Evasion ~28%
Hybrid (expected)
DR >95% FPR <3% Evasion <5%
51.508 Secure CPS · SWaT Defense · Implementation & Evaluation

## Slide 29
References
[1]
S. Adepu and A. Mathur
"Using Process Invariants to Detect Cyber Attacks on a Water Treatment System"
IFIP SEC, Ghent, Belgium, 2016. (Paper #88 — SWaT invariant baseline)
[2]
S. Adepu and A. Mathur
"Distributed Detection of Single-Stage Multipoint Cyber Attacks in a Water Treatment Plant"
ACM AsiaCCS, Xi'an, China, 2016. (DAD invariant design)
[3]
J. H. Castellanos, M. Ochoa, A. A. Cardenas, O. Arden, and J. Zhou
"Constrained Concealment Attacks against Reconstruction-based Anomaly Detectors in ICS"
ACM ACSAC, Austin, USA, 2020. (Paper #31 — adversarial AE evasion) github.com/scy-phy/ICS-Evasion-Attacks
[4]
W. Alsabbagh, S. Amogbonjaye, D. Urrego, and P. Langendörfer
"A Stealthy False Command Injection Attack on Modbus based SCADA Systems"
IEEE CCNC, Las Vegas, USA, 2023. (Paper #9 — Modbus FCI attack)
[5]
A. Carcano, A. Coletta, M. Guglielmi, M. Masera, I. N. Fovino, and A. Trombetta
"A Multidimensional Critical State Analysis for Detecting Intrusions in SCADA Systems"
IEEE Trans. Industrial Informatics, vol. 7, no. 2, pp. 179–186, May 2011. DOI: 10.1109/TII.2010.2098415
[6]
D. I. Buzhinsky and V. Vyatkin
"Automatic Inference of Finite-State Plant Models from Traces and Temporal Properties"
IEEE Trans. Industrial Informatics, vol. 13, no. 4, pp. 1521–1530, Aug. 2017. DOI: 10.1109/TII.2017.2670001
[7]
iTrust, Centre for Research in Cyber Security, SUTD
"SWaT: Secure Water Treatment Testbed"
Singapore University of Technology and Design. https://itrust.sutd.edu.sg/testbeds/secure-water-treatment-swat/
51.508 Secure Cyber Physical Systems | SWaT Defense | References

## Slide 30
CPS Cyber Attack Recovery
Methods, Taxonomy & Application to SWaT
Shallow Recovery
Safe-state + failover
Deep Recovery
Dedicated recovery controller
State Estimation
Kalman / Luenberger observers
NIST SP 800-82r3
OT incident response framework
Key finding (ACM Survey 2024): Most CPS security research focuses on detection — recovery is the least studied phase. Shallow recovery (safe state + PLC failover) is deployable in SWaT immediately; deep recovery via secure state estimation is the research frontier.
51.508 Secure Cyber Physical Systems | iTrust Lab, SUTD | AY2025/26 Term 2
51.508 Secure CPS · SWaT Recovery Research

## Slide 31
Recovery Taxonomy: Shallow vs Deep
ACM Computing Surveys (2024) surveyed 30 CPS recovery papers — two fundamental strategies identified
Shallow Recovery
Does NOT require a dedicated recovery controller.
Uses pre-designed safe states & redundancy.
1
Safe-State Transition
Pre-defined fail-safe actuator values per stage written to PLC registers immediately on alert. No computation required — purely deterministic lookup.
2
Hot-Standby PLC Failover
Primary PLC1A isolated; EtherNet/IP handshake activates PLC1B (mirror image of ladder logic + last safe register state). <3 s switchover.
3
Network Isolation (Containment)
iptables rules drop all Modbus TCP port 502 traffic from attacker MAC. VLAN isolation enforced at L2 switch within seconds of alert.
4
Checkpoint & Restore
Kong et al. (ICCPS 2018): periodic system state snapshots to trusted storage; rollback to last valid checkpoint post-attack. Applicable to SWaT HMI + historian.
5
Manual Operator Override
Physical bypass of all digital commands; local operator restores process using P&ID reference. Last resort — used if PLC1B failover also compromised.
Deep Recovery
Requires a dedicated recovery controller that
runs in parallel and actively restores the system.
1
Secure State Estimation (SSE)
Luenberger / Kalman observers reconstruct true plant state from uncorrupted sensor subsets during the attack window. Bridges the gap between alert and verified safe state.
2
Model Predictive Control (MPC) Recovery
He et al. (2021): resilient self-triggered MPC adjusts update frequency and reconstructs input signals during FDI attacks. Proven input-to-state stability.
3
Sliding Mode Observer (SMO)
Adaptive-gain SMO reconstructs sensor and actuator attacks online in real time; cleans corrupted measurements before feeding back to controller.
4
Learn-to-Respond (RL-based)
Liu et al. (RTSS 2023): sequence-predictive recovery uses RL to learn optimal recovery sequences from attack scenarios. Suited for novel/unseen attack patterns.
5
Invariant-Guided Reconstruction
After safe state confirmed, re-enable sensors one at a time; accept reading only if all P1 invariants are satisfied with new value. Physics-constrained re-entry.
51.508 Secure CPS · SWaT Recovery Research · Recovery Taxonomy

## Slide 32
Secure State Estimation (SSE) Methods
Core academic methods for reconstructing plant state when sensors are under attack
Luenberger Observer
Lu & Yang, Info. Sci. 2017
Augments system state with attack signals as extra states. Switched observer selects attack-free sensor subsets per cycle. Guarantees exponential convergence to true state under sparse attacks.
✓ Strengths
▸ Provably stable (LMI conditions)
▸ Handles time-varying attack locations
▸ Low computation — suitable for PLC timing
✗ Limitations
▸ Requires linear system model of SWaT P1 hydraulics
▸ Degrades if > p/2 sensors attacked
SWaT applicability
SWaT P1 linearises well around operating point. FIT101, LIT101 are the key sensors — SSE can reconstruct from pressure/flow cross-readings.
Kalman-based Secure Estimator
Chang, Hu & Tomlin, ArXiv 2015
Combines classical error-correction (decoding from corrupted codewords) with Kalman filter. Treats attack as sparse coding error; recovers true state if system is 2s-sparse observable.
✓ Strengths
▸ Handles Gaussian noise naturally
▸ Optimal for stochastic systems
▸ Extended Kalman generalises to nonlinear
✗ Limitations
▸ Computationally heavier than Luenberger
▸ Requires accurate noise covariance matrices
SWaT applicability
Extended Kalman filter applicable to nonlinear SWaT tank dynamics (LIT101 ODE). Well-suited for Paper #31 sensor spoofing scenario.
Sliding Mode Observer (SMO)
IntechOpen 2019; AdaptiveCPS 2016
Finite-time convergent observer using sliding mode theory. Reconstructs both sensor and actuator attacks online. Super-twisting variant handles time-varying attacks without a priori knowledge of attack waveform.
✓ Strengths
▸ Reconstructs attack signal explicitly
▸ No system model of attack required
▸ Fast — finite-time convergence
✗ Limitations
▸ Chattering effect needs damping
▸ Requires continuous sensor availability
SWaT applicability
Directly estimates the δ injected by Paper #31's adversarial AE. Reconstructed δ can be subtracted from readings to recover clean sensor values.
51.508 Secure CPS · SWaT Recovery Research · SSE Methods

## Slide 33
Fundamental Limit: 2s-Sparse Observability
How many sensors can be corrupted before state reconstruction becomes impossible?
Theorem (Shoukry & Tabuada, IEEE TAC 2016)
The true state of a CPS can be uniquely recovered despite sensor attacks on at most s sensors IF AND ONLY IF the system remains observable after removing any 2s sensor rows from the output matrix C. This is called 2s-sparse observability.
SWaT P1 Sensors — Sparse Observability Analysis
Sensor
Physical Role
Criticality
Standalone?
Recovery Approach
FIT101
Raw water flow rate
HIGH
Derivable from P101 state + LIT101 Δ
LIT101
Tank level
HIGH
No direct redundancy — physics model needed
MV101
Motorised inlet valve (coil)
MEDIUM
PLC register directly readable (not only sensor)
P101
Primary pump (coil)
MEDIUM
PLC register directly readable (not only sensor)
P102
Backup pump (coil)
LOW
Mirrors P101 state — 1-1 redundancy
SWaT P1 conclusion: P1 has 5 sensors/actuators. For SSE to work under Paper #9's attack (which targets MV101 + P101 coils), we need the system to be 2×1 = 2-sparse observable — i.e. state recoverable after removing any 2 sensor rows. SWaT P1 satisfies this since FIT101 and LIT101 together with the process ODE fully determine the tank state even without actuator coil readings.
51.508 Secure CPS · SWaT Recovery Research · 2s-Sparse Observability

## Slide 34
Proposed: Invariant-Guided Sensor Reconstruction
A SWaT-specific deep recovery method — physics-constrained re-entry after safe state is reached
Algorithm: Invariant-Guided Re-entry
1
Reach Safe State
All P1 actuators driven to known-safe values (MV101 CLOSED, P101/102 OFF). Wait 2 PLC cycles for register confirmation.
2
Isolate Attack Channel
Modbus TCP blocked. PLC1B is now primary. All Modbus traffic to PLC1A dropped at iptables.
3
Reconstruct LIT101 from ODE
Use process model: dL/dt = Q_in - Q_out. Since pumps are OFF, Q_in=Q_out=0, so LIT101 = last_valid_LIT101. Cross-check with historical trend.
4
Re-enable sensors sequentially
Enable FIT101 first (reads 0 — valve closed). Accept if consistent with I-6. Then enable MV101 coil read. Accept if FIT101 responds correctly on valve open.
5
Invariant-gated acceptance
Each sensor reading accepted only if ALL 8 invariants remain satisfied for 5 consecutive cycles. Any violation → reject + hold last valid.
6
Resume normal control
Transfer control back to full PLC1B ladder logic. Log full incident timeline. Notify security team for forensics.
P1 Tank ODE Model
dL/dt = (Q_in - Q_out) / A_tank Q_in = MV101_state × FIT101_reading Q_out = P101_state × rated_flow A_tank ≈ 1.5 m² (SWaT P1 spec)
In safe state: MV101=0, P101=0 → dL/dt = 0
LIT101 is constant → predictable, verifiable.
Why Physics-Constrained Re-entry Matters
▸ Attacker may still have Modbus MITM active — naively trusting sensor replies on resume would re-expose the system
▸ Invariant-gated acceptance means a compromised sensor reading is rejected before it reaches the PLC control loop
▸ Sequential re-enablement limits blast radius: if FIT101 alone is still spoofed, only FIT101 is rejected — P1 resumes partially
▸ No external trusted sensor needed — the process ODE itself provides ground truth during the safe-state window
▸ Matches ICS/OT incident response principle: 'verify before restore' (NIST SP 800-82r3 §6.3)
51.508 Secure CPS · SWaT Recovery Research · Invariant-Guided Reconstruction

## Slide 35
Industry Framework: NIST SP 800-82r3
Guide to OT Security (Sep 2023) — our recovery design maps directly to its 5 recovery principles
NIST SP 800-82r3 Principle
Our SWaT Recovery Implementation
RC.RP-1: Recovery plan executed during/after incident
Pre-coded recovery_agent.py executes automatically on ALERT — no human in the loop required for Phase 1 containment
RC.IM-1: Recovery strategies incorporate lessons learned
Full incident log written to tamper-evident WORM storage (historian); each attack-recovery cycle updates threshold for future detection
RS.CO-3: Information shared consistently with response plans
SCADA HMI alarm triggers email + SMS to iTrust lab engineer; PLC1B takeover reflected in all monitoring dashboards within 1 cycle
RS.AN-1: Notifications from detection systems investigated
Fusion engine logs: which layer fired, sensor snapshot at T=alert, ARP table state — sufficient for post-incident forensic root cause analysis
RC.CO-3: Recovery communicated to stakeholders/authorities
iTrust lab security coordinator notified automatically; full recovery event written to SWaT incident registry for research analysis
ICS/OT-specific principle (SANS 2024): Unlike IT incident response, OT recovery must be engineering-led and safety-first. Isolating a PLC at the wrong moment can cause immediate physical harm. Our recovery sequence respects this — containment is network-level first, PLC-level second, only after safe state is verified.
51.508 Secure CPS · SWaT Recovery Research · NIST SP 800-82r3 Alignment

## Slide 36
Real-World Recovery Case Studies
What actually happened in water/ICS attacks — and what recovery looked like
💧 Oldsmar, Florida Water Plant
Feb 2021
Attack
Attacker remotely modified NaOH level in SCADA to 111× normal via TeamViewer remote access.
Recovery
Operator noticed HMI cursor moving unexpectedly — manually reverted setpoint within minutes. No physical damage. Highlights value of operator monitoring alongside automated systems.
Lesson for SWaT
Human-in-the-loop recovery can be faster than automated if operator is trained and monitoring. But reliance on human observation alone is insufficient — automated alert would have fired before cursor movement.
🏭 Texas Water Utilities
Apr 2024
Attack
Russian-linked hackers targeted Unitronics PLCs (exposed SCADA). One plant tank overflowed; SCADA systems disrupted.
Recovery
Manual override to local control. Physical inspection of all actuator states. Took days to verify system integrity before resuming automated control. No cryptographic verification of PLC firmware.
Lesson for SWaT
No hot-standby PLC, no automated safe-state — recovery took days vs our target of <15s. Firmware integrity checking post-incident critical. Our design adds cryptographic PLC1B verification step.
⚛️ Stuxnet (Natanz, Iran)
2009–2010
Attack
Centrifuge speed manipulation while spoofing normal readings to HMI. Classic Paper #9 + #31 combined in practice.
Recovery
Operators unaware of attack for months — no process invariant checker existed. Physical centrifuge damage discovered only after fact. Forensic reconstruction of attack timeline took years.
Lesson for SWaT
Invariant-based detection would have caught actuator/sensor inconsistency immediately. Our I-7 equivalent (pump ON + valve state mismatch) fires in <3 cycles. Recovery plan must pre-exist attack — post-hoc is too late.
51.508 Secure CPS · SWaT Recovery Research · Case Studies

## Slide 37
Recovery Methods — Comparison Matrix for SWaT
Evaluating each method against SWaT's specific constraints: real-time PLC timing, Modbus attack, sensor spoofing
Method
Recovery
Time
Requires
Model
Handles
Spoofed Sensors
Deployable
in SWaT
Paper #9
Coverage
Paper #31
Coverage
Safe State + Failover
(Shallow — Ours)
< 15s
No
Partial ⚠️
✓ Yes
✓ Full
Partial ⚠️
Checkpoint & Restore
(Kong et al. 2018)
Minutes
No
No ✗
✓ HMI only
✓ Full
No ✗
Luenberger SSE
(Lu & Yang 2017)
1–3 cycles
Linear
✓ Yes
Feasible
✓ Full
✓ Full
Kalman Secure Est.
(Chang et al. 2015)
1–3 cycles
Stochastic
✓ Yes
Feasible
✓ Full
✓ Full
Sliding Mode Obs.
(Adaptive 2016)
< 1 cycle
Partial
✓ Explicit
Feasible
✓ Full
✓ Best
MPC Recovery
(He et al. 2021)
Multi-cycle
Full MPC
✓ Yes
Complex
Partial
✓ Full
Inv-Guided Re-entry
(Proposed — Ours)
< 30s
ODE only
✓ Yes
✓ Yes
✓ Full
✓ Full
Recommended for SWaT: Deploy Shallow (Safe State + Failover) immediately — zero model requirements. Layer in Invariant-Guided Re-entry (proposed) for sensor-level recovery. Luenberger SSE is the academic stretch goal for full deep recovery.
51.508 Secure CPS · SWaT Recovery Research · Comparison Matrix

## Slide 38
Integrated Recovery Architecture — SWaT
Combining shallow + deep recovery in a single automated pipeline triggered by the hybrid detector
DETECT
→
Hybrid detector
fusion score ≥ 1.5
0s
CONTAIN
→
iptables block
VLAN isolation
<3s
SAFE STATE
→
Actuator reset
PLC registers
<5s
FAILOVER
→
PLC1B takes
control (EIP)
<8s
RECONSTRUCT
→
SSE + invariant-
guided re-entry
<30s
RESUME
All invariants
pass 5+ cycles
<60s
Path A — Shallow Recovery (Immediate)
Deployed in SWaT today — no additional development needed
▸ recovery_agent.py runs automatically on ALERT
▸ iptables: drop port 502 from attacker MAC
▸ Write safe-state dict to PLC1 coil registers via pyModbus
▸ EtherNet/IP handshake activates PLC1B as primary
▸ Human engineer verifies physically before final resume
▸ Total time target: < 15 seconds
Path B — Deep Recovery (Research Extension)
Extends shallow — adds sensor-level reconstruction
▸ Luenberger SSE runs on parallel thread during attack
▸ Reconstructs LIT101/FIT101 from uncorrupted subset
▸ Invariant-guided re-entry gates each sensor re-acceptance
▸ ODE-predicted LIT101 compared with SSE estimate
▸ Accept sensor only if ODE, SSE, and invariant agree
▸ Full automated resume — no human required
51.508 Secure CPS · SWaT Recovery Research · Integrated Architecture

## Slide 39
Implementation Plan & Open Research Challenges
What we can build now vs what remains as open problems worth studying
Buildable Now — Project Deliverables
READY
recovery_agent.py
Automated safe-state writer + iptables containment + PLC1B handshake trigger. Uses pyModbus + pyEthernetIP.
READY
ode_estimator.py
Discrete ODE integrator for LIT101 using PLC1B register reads during recovery window. Predicts expected tank level.
LAB NEEDED
sse_observer.py
Luenberger observer for P1 linearised around operating point. Requires P1 A, B, C matrices from system ID.
READY
reentry_gate.py
Invariant-gated sensor acceptance on recovery. Reads each sensor, validates against all 8 invariants × 5 cycles before accepting.
DEMO
Full integration test
Run simulated Paper #9+#31 attack → trigger detector → execute recovery pipeline → measure TTR on SWaT testbed.
Open Research Challenges
?
System identification for SWaT P1
Luenberger SSE requires state-space matrices (A, B, C). SWaT uses nonlinear hydraulics — linearisation around operating point needed. Requires access to SWaT normal data + PLC ladder logic.
?
Multi-stage cascading recovery
Paper #9 can attack all 6 stages simultaneously. Our design recovers P1 only. Multi-stage parallel recovery with cross-stage invariant checking is an open problem.
?
Adversarial recovery evasion
An advanced attacker could time their attack to coincide with the recovery window, spoofing the ODE-predicted values during invariant-guided re-entry. Counter: authenticated sensor channels.
?
Recovery time guarantees
Academic papers on CPS recovery rarely provide hard real-time guarantees for embedded PLC environments. Formal verification of recovery timing is open (RTAS/RTSS venue).
?
Post-attack forensics
After recovery, how do we determine the full attack timeline for legal/attribution purposes? Tamper-evident Modbus traffic logging and PLC register versioning needed.
51.508 Secure CPS · SWaT Recovery Research · Implementation & Challenges

## Slide 40
Recovery Research References
[R1]
ACM Computing Surveys 2024 — Recovery from Adversarial Attacks in CPS: Shallow, Deep and Exploratory Works. doi:10.1145/3653974
[R2]
A. Y. Lu & G. H. Yang — Secure State Estimation for CPS under Sparse Sensor Attacks via Switched Luenberger Observer. Information Sciences 417, 2017.
[R3]
A. Y. Lu & G. H. Yang — Secure Luenberger-like Observers for CPS under Sparse Actuator and Sensor Attacks. Automatica 98, 2018.
[R4]
Y. Shoukry & P. Tabuada — Event-triggered State Observers for Sparse Sensor Noise/Attacks. IEEE TAC 61(8), 2016. (2s-sparse observability theorem)
[R5]
Y. H. Chang, Q. Hu & C. Tomlin — Secure Estimation based Kalman Filter for CPS against Adversarial Attacks. ArXiv 2015.
[R6]
NIST SP 800-82 Revision 3 — Guide to Operational Technology (OT) Security. NIST, September 2023. https://csrc.nist.gov/pubs/sp/800/82/r3/final
[R7]
F. Kong et al. — Cyber-Physical System Checkpointing and Recovery. ICCPS 2018. IEEE.
[R8]
M. Liu et al. — Learn-to-Respond: Sequence-Predictive Recovery from Sensor Attacks in CPS. RTSS 2023. IEEE.
[R9]
A. Staves et al. — A Cyber Incident Response and Recovery Framework for ICS Operators. Int. J. Critical Infrastructure Protection 37, 2022.
[R10]
SANS Institute — 2024 State of ICS/OT Cybersecurity. SANS Institute, May 2024. https://www.sans.org/blog/the-2024-state-of-ics-ot-cybersecurity
[R11]
ScienceDirect 2024 — Attack Isolation in a Water Treatment Plant (SWaT). IFAC-PapersOnLine. doi:10.1016/j.ifacol.2024.07...
51.508 Secure CPS · SWaT Recovery Research · References